## 说明(clarification)
迈格瑞能MEGA系列PCS与EMS的Modbus协议 Modbus protocol for MEGAREVO's "MEGA series" PCS with EMS
规则说明： Rule Description:
1、串口通信地址默认为 1。(可在屏幕的高级设置中修改) 1. The serial port communication address defaults to 1. (Can be modified in the advanced settings of the screen)
2、控制字为可读可写，状态字为只读。 2. The control word is readable and writable, and the status word is read-only.
3、支持ModbusRTU和ModbusTCP通信方式，支持读命令：0x03、0x04；支持写命令：0x06、0x10。 3、Support ModbusRTU and ModbusTCP communication mode, support read command: 0x03; support write command: 0x06, 0x10.
4、Modbus-TCP/IP协议，默认端口：502。服务IP：（192.168.1.100）。IP地址可配置。 4、Modbus-TCP/IP protocol, default port: 502. service IP: (192.168.1.100). IP address is configurable.
5、数据类型：U16(无符号16位数据)、S16(有符号16位数据)、char(字符数据)、str(字符串数据)。 5、data type: U16 (unsigned 16-bit data), S16 (signed 16-bit data), char (character data), str (string data).
6、点表颜色说明： 6. Point Table Color Explanation: | 黄色(和上一版本对比是内容修改) Yellow (Content modification compared to the previous version) | 蓝色(和上一版对比是改预留) Blue (Preserved compared to the previous version) | 绿色(和上一版对比是新增) Green (New addition compared to the previous version)
版本 Version | 修改时间 Modify Time | 修改内容 Contents of the modification | 拟定人 Author
V1.0 | 2023-11-07 | 制定新版PCS Modbus点表 Develop a new version of the PCS Modbus point table. | 叶永健 YeYongJian
V3.0.0 | 2024-04-15 | 按标准化版本进行迭代，添加英文 Iterate on standardised versions, add English translations | 黎培荣 Peirol
V3.0.1 | 2024-04-24 | 新增柴发容量，更新告警字 Additional Generator Capacity, Update Alarm Word | 黎培荣 Peirol
V3.0.2 | 2024-04-30 | 标注告警字响应动作 Label the warning word response action | 黎培荣 Peirol
V3.0.3 | 2024-06-18 | 协议标准化；新增Modbus协议版本；优化输出电压等级；新增心跳信号 Protocol standardisation; new Modbus protocol version; optimised output voltage level; add heartbeat signal | 黎培荣 Peirol
V3.0.4 | 2024-08-06 | 新增12V铅酸电池设置参数读写；新增备电模式设置参数读写；更正BMS告警字3内容 Add 12V lead-acid battery setting parameter reading and writing; Add backup battery mode setting parameter reading and writing; Modify the content of BMS alarm word 3. | 黎培荣 Peirol
V3.0.5 | 2024-10-30 | 修改"后备充电功率"为"备电充电功率(电网)"；新增月循环日期，备电充电功率(发电机) Modified ‘Backup charging power’ to ‘Backup charging power (grid)’; added monthly cycle date, backup charging power (generator) | 黎培荣 Peirol
V3.0.6 | 2024-11-05 | 告警字4更新，新增硬件过温故障位 Alarm word 4 updated with new Hardware over temperature fault bit | 黎培荣 Peirol
V3.0.7 | 2024-11-16 | 告警字4更新，新增硬件过流，逆变过载，电池过流故障位 Alarm Word 4 Update: Added fault bits for hardware overcurrent, inverter overload, and battery overcurrent. | 黎培荣 Peirol
V3.0.8 | 2024-11-26 | 开关状态字更新，新增主从机状态 Switch status words updated with new master/slave statuses | 黎培荣 Peirol
V3.0.9 | 2024-12-25 | 新增DC接触器辅助触点屏蔽使能；新增故障恢复延时使能；新增频繁故障拓机使能；新增故障重启次数设置 Add DC contactor shielding enable；Add Fault Recovery Delay Enable;Add Frequent Fault Mapping Enable;Add Fault restart frequency; | 叶永健 Yaron
V3.0.9 | 2024-12-25 | 新增DC接触器辅助触点屏蔽使能；新增故障恢复延时使能；新增频繁故障拓机使能；新增故障重启次数设置 Add DC contactor shielding enable；Add Fault Recovery Delay Enable;Add Frequent Fault Mapping Enable;Add Fault restart frequency; | 叶永健 Yaron
V3.0.10 | 2024-12-25 | 添加告警字5；添加消除故障指令 Add register 2119 alarm word5; Add fault elimination command | 叶永健 Yaron
V3.0.11 | 2025-02-13 | 添加变流器防逆流使能；添加功率容差；添加远程ATS信号；更新工作模式关于瞬态扩容的描述；更正电表功率倍率 Add Converter Anti-Reverser Flow Enable; Add power tolersnce;Add Remote ATS Signal;Update the description of transient expansion in the working mode;Correct the power multiplier of the electricity meter | 叶永健 Yaron
V3.0.12 | 2025-04-02 | 添加削峰填谷时间段功能设置； Add peak shaving time period function settings; | 叶永健 Yaron
V3.0.13 | 2025-06-11 | 添加有功-频率下垂系数； 添加无功-电压下垂系数； Add Active Power - Frequency Droop Coefficient; Add Reactive Power - Voltage Droop Coefficient; | 叶永健 Yaron
V3.0.14 | 2025-06-23 | 恢复寄存器2214~2218预留的寄存器； Restore the reserved registers of 2214~2218; | 叶永健 Yaron
V3.0.15 | 2025-08-11 | 添加负载电量统计数据（2560~2575寄存器）; 原PCS充放电量统计变更为电网充放电量统计； Add load power statistics data (registers 2560-2575); The original PCS charging and discharging capacity statistics have been changed to grid charging and discharging capacity statistics; | 叶永健 Yaron
V3.0.16 | 2025-09-11 | 负载频率取消预留； 添加正绝缘阻抗和负绝缘阻抗读取； Cancel the reserved load frequency; Add positive and negative insulation impedance readings; | 叶永健 Yaron
V3.0.17 | 2025-09-18 | 添加功率限制关联方式； 添加柴发并入功率变化率； 添加并离网切换停机使能和并离网切换停机延时时间； 更改有功-频率下垂系数和无功-频率下垂系数为预留; Add "Power Limit Link Mode" Add diesel generator and power change rate; Add "Grid On/Off Switching Shutdown Enable" and "Grid On/Off Switching Shutdown Delay Time"; Change the active frequency droop coefficient and reactive frequency droop coefficient to reserve | 叶永健 Yaron

## 产品信息(Product Information)
MEGA
Fuction code | Register (DEC/HEX) | Byte | Item | range | 注释 annotation | 解析 analysis
0x03 0x04 | 2000-2004 （07D0-07D4） | 10 | 变流器名称(预留) Converter Name(Reserved) | “MEGA 0500” | MEGA0500、MEGA0500T——并网机型，500是机器功率等级500kw MEGA0500TS——并离网机型， 500是机器功率等级500kw MEGA0500, MEGA0500T - Grid-connectedD4:F6 models, 500 is the power class of the machine 500kw. MEGA0500TS - Grid-connected model, 500 is the power class of the machine 500kw. | 举例:01 03 0A 4D 45 47 41 2D 54 53 35 30 30 8F 36 使用ASCII码值进行解析 4D 45 47 41 2D 54 53 35 30 30 M E G A - T S 5 0 0 2000:4D45--19781 2001:4741--18241 2002:2D54--11604 2003:5335--21301 2004:3030--12336 | Example:01 03 0A 4D 45 47 41 2D 54 53 35 30 30 8F 36 Parsing using ASCII values 4D 45 47 41 2D 54 53 35 30 30 M E G A - T S 5 0 0 2000:4D45--19781 2001:4741--18241 2002:2D54--11604 2003:5335--21301 2004:3030--12336
“MEGA-T0500T”
“MEGA-TS0500”
| 2005-2009 （07D5-07D9） | 10 | 厂家名称 Manufacture name | "MEGAREVO" | 4D 45 47 41 52 45 56 4F 20 20
| 2010-2015 （07DA-07E0） | 12 | SN | “F12200000001” | 46 31 32 32 30 30 30 30 30 30 30 31
| 2017-2022 （07E1-07E6） | 12 | 变流器软件版本 Converter software version
| 2023-2028 （07E7-07EC） | 12 | 监控软件版本 Monitoring software version |  | 56 31 30 35 42 35 30 30 44 30 30 38 V105B500D008
| 2029-2030 （07ED-07EE） | 4 | Modbus协议版本 Modbus Protocol Version | "V305" | 56 33 30 35 V305
| 2031-2036 (07EF-07F5) | 12 | 变流器名称 Converter Name | PCS-500 | PCS-500——并网机型，500是机器功率等级500kw PCS-TS-500, PCS-TS-T-500——并离网机型， 500是机器功率等级500kw PCS-500 - Grid-connected models, 500 is the power class of the machine 500kw. PCS-TS-500, PCS-TS-T-500 - Grid-connected model, 500 is the power class of the machine 500kw. | 50 43 53 2D 35 30 30 20 20 20 20 20 | 不足12位字符，辅以一些空格 Less than 12 characters, supplemented by some spaces
|  |  |  | PCS-TS-500 |  | 50 43 53 2D 54 53 2D 35 30 30 20 20
|  |  |  | PCS-TS-T-500 |  | 50 43 53 2D 54 53 2D 54 2D 35 30 30

## 点表(Point Table)
MEGA
Fuction code | Register(DEC/HEX) | Byte | Type | Item | range | rate | Read/Write | Fuction code | Register(DEC/HEX) | Byte | Type | Item | range | Range Translate | rate | Read/Write | Note | Fuction code | Register(DEC/HEX) | Byte | Type | Item | Description | Description | Rate | Read/Write | Note
0x04 | PCS 告警字、PCS状态字、BMS告警字 PCS Alarm Word，PCS Status Word，BMS Alarm Word | [7 empty] | PCS 设置参数 读取/下发 PCS Setting parameter read/write | [8 empty] | 削峰填谷 Peak Valley
| 2100(0834) | 2 | U16 | 告警字1 Alarm Word 1 | 0xFFFF | 1 | Read | 0x04 | 2659(0A63) | 2 | U16 | 容量 Capacity | [30, 630] | [30, 630] | 1kW | Read
| 2101(0835) | 2 | U16 | 告警字2 Alarm Word 2 | 0xFFFF | 1 | Read | 0x03 0x06 | 2761(0AC9) | 2 | S16 | 恒功率(AC) Constant Power (AC) | 以实际功率下发，范围为机型容量的[-110%, 110%] | With actual power delivery, the range is [-110%, 110%] of the model capacity | 0.1kW | Read/Write |  | 时间段1-10的寄存器地址规则为：寄存器基地址+0x0F*(N-1)。N是时间段序号，N的范围为[1,10]。 The register address rule for time periods 1-10 is as follows: register base address + 0x0F * (N-1), where N is the time period index ranging from 1 to 10. 例：读时间段1的"开始时间"，其寄存器地址为：0x0D53+0x0F*(1-1)=0x0D53；读时间段3的"结束时间"，其寄存器地址为：0xD54+0x0F*(3-1)=0xD72; Example: Read the "start time" of time period 1, and its register address is: 0x0D53+0x00F * (1-1)=0x0D53; Read the 'end time' of time period 3, and its register address is: 0xD54+0x0F * (3-1)=0xD72;
| 2102(0836) | 2 | U16 | 告警字3 Alarm Word 3 | 0xFFFF | 1 | Read |  | 2762(0ACA) | 2 | U16 | 输出无功方式 Output Reactive Power Mode | 0：不可调节 1：功率因数 2：无功功率 | 0: Non adjustable 1: power factor (PF) 2: reactive power (P) | 1 | Read/Write
| 2103(0837) | 2 | U16 | 告警字4 Alarm Word 4 | 0xFFFF | 1 | Read |  | 2763(0ACB) | 2 | S16 | 输出功率因数 Output power factor | [-100, 100] | [-100, 100] | 0.01 | Read/Write |  | 0x03 0x04 0x06 | 削峰填谷模式-时间段参数设置 Peak shaving mode - Time period parameter setting
| 2104(0838) | 2 | U16 | 开关状态字 Switch Status Word | 0xFFFF | 1 | Read |  | 2764(0ACC) | 2 | S16 | 输出无功功率 Output reactive power | 以实际功率下发，范围为机型容量的[-110%, 110%] | With actual power delivery, the range is [-110%, 110%] of the model capacity | 0.1kvar | Read/Write |  |  | 3410 (0D52) | 2 | U16 | 时间段使能 Time period enable | 0:禁止;1:使能 | 0:Disable;1:Enable | 1 | Read/Write | 时间段1 Time period 1
| 2105(0839) | 2 | U16 | PCS状态字 PCS Status Word | 0xFFFF | 1 | Read |  | 2765(0ACD) | 2 | U16 | PCS并网方式 Grid connected mode of PCS | 1：离网； 2：并网； 3：并离网 | 1: Grid-off 2: Grid-on 3: Automatic | 1 | Read/Write |  |  | 3411 (0D53) | 2 | U16 | 开始时间 Start time | [0x0000, 0x173B] 小时在高8位，分钟在低8位 | [0x0000, 0x173B] Hours in the high 8 bits, minutes in the low 8 bits | 1 | Read/Write
| 2106(083A) | 2 | U16 | 外设状态 Peripheral Status | 0xFFFF | 1 | Read |  | 2766(0ACE) | 2 | U16 | 远程EPO Remote EPO | 1：执行紧急关机(EPO) 2：清除紧急关机(EPO) | 1: Emergency Power Off (EPO) 2: Clear Emergency Power Off | 1 | Read/Write |  |  | 3412 (0D54) | 2 | U16 | 结束时间 Stop time | [0x0000, 0x173B] 小时在高8位，分钟在低8位 | [0x0000, 0x173B] Hours in the high 8 bits, minutes in the low 8 bits | 1 | Read/Write
| 2107(083B) | 2 | U16 | 监控告警字 Monitor Alarm Word | 0xFFFF | 1 | Read |  | 2767(0ACF) | 2 | S16 | 恒流值 Constant current | [-1500, 1500] | [-1500, 1500] | 1A | Read/Write |  |  | 3413 (0D55) | 2 | S16 | 功率 Power | 以实际功率下发，范围为机型容量的 [-110%, 110%] | With actual power delivery, the range is [-110%, 110%] of the model capacity | 0.1kW | Read/Write
| 2108(083C) | 2 | U16 | 电池告警字1 BMS Alarm Word 1 | 0xFFFF | 1 | Read |  | 2768(0AD0) | 2 | U16 | 功率控制类型 Power control type | 0:预留 1:预留 2:正负功率 3:恒流 4:恒压 | 0: Reserve; 1: Reserve; 2: Positive and negative power (CP_AC); 3: Constant current (CC); 4: Constant voltage (CV) | 1 | Read/Write |  |  | 3414 (0D56) | 2 | U16 | 预留 (Reserve)
| 2109(083D) | 2 | U16 | 电池告警字2 BMS Alarm Word 2 | 0xFFFF | 1 | Read |  | 2769(0AD1) | 2 | U16 | 遥控开关机 Remote control turn on/off | 0x5555——变流器开机 0xAAAA——变流器关机 0x55AA——变流器待机 | 0x5555 - Converter Turn On 0xAAAA - Converter Shutdown 0x55AA - Converter Standby | 1 | Read/Write | 下发待机指令会将恒功率置0 Executing the standby command sets the constant power to 0 |  | 3415 (0D57) | 2 | U16 | 预留 (Reserve)
| 2110(083E) | 2 | U16 | 电池告警字3 BMS Alarm Word 3 | 0xFFFF | 1 | Read |  | 2770(0AD2) | 2 | U16 | 控制模式 Control mode | 0：本地 1：远程 | 0：Local 1：Remote | 1 | Read/Write |  |  | 3416 (0D58) | 2 | U16 | 预留 (Reserve)
| 2111(083F) | 2 | U16 | 电池告警字4 BMS Alarm Word 4 | 0xFFFF | 1 | Read |  | 2771(0AD3) | 2 | U16 | 并机 Parallel | 0：禁止 1：使能 | 0：Disable 1：Enable | 1 | Read/Write |  |  | 3417 (0D59) | 2 | U16 | 预留 (Reserve)
| 2112(0840) | 2 | U16 | 电池告警字5 BMS Alarm Word 5 | 0xFFFF | 1 | Read |  | 2772(0AD4) | 2 | U16 | 设备号 Machine Number | 0：主机；1~8为从机 | 0：Master; 1~8：Slaves | 1 | Read/Write |  |  | 3418 (0D5A) | 2 | U16 | 预留 (Reserve)
| 2113(0841) | 2 | U16 | 电池告警字6 BMS Alarm Word 6 | 0xFFFF | 1 | Read |  | 2773(0AD5) | 2 | U16 | 恒压值 Constant voltage | [400, 850] | [400, 850] | 1V | Read/Write |  |  | 3419 (0D5B) | 2 | U16 | 预留 (Reserve)
| 2114(0842) | 2 | U16 | 电池告警字7 BMS Alarm Word 7 | 0xFFFF | 1 | Read |  | 2774(0AD6) | 2 | U16 | 输出电压等级 Output voltage level | [180, 220] (200V变压器) [180, 235] (208V变压器) [350, 440] (400V变压器) [440, 520] (480V变压器) | [180, 220] (200V's Transformer) [180, 235] (208V's Transformer) [350, 440] (400V's Transformer) [440, 520] (480V's Transformer) | 1V | Read/Write | 仅离网模式可更改 Only off-grid mode can be changed |  | 3420 (0D5C) | 2 | U16 | 预留 (Reserve)
| 2115(0843) | 2 | U16 | 电池告警字8 BMS Alarm Word 8 | 0xFFFF | 1 | Read |  | 2775(0AD7) | 2 | U16 | 输出频率等级 Output frequency level | [4000, 6000] | [4000, 6000] | 0.01Hz | Read/Write |  |  | 3421 (0D5D) | 2 | U16 | 预留 (Reserve)
| 2116(0844) | 2 | U16 | 电池告警字9 BMS Alarm Word 9 | 0xFFFF | 1 | Read |  | 2776(0AD8) | 2 | U16 | 充电功率限制 Charge Power Limit | 以实际功率下发，范围为机型容量的[-110%, 110%] | With actual power delivery, the range is [-110%, 110%] of the model capacity | 0.1kW | Read/Write |  |  | 3422 (0D5E) | 2 | U16 | 预留 (Reserve)
| 2117(0845) | 2 | U16 | 电池告警字10 BMS Alarm Word 10 | 0xFFFF | 1 | Read |  | 2777(0AD9) | 2 | U16 | 放电功率限制 Discharge Power Limit | 以实际功率下发，范围为机型容量的[-110%, 110%] | With actual power delivery, the range is [-110%, 110%] of the model capacity | 0.1kW | Read/Write |  |  | 3423 (0D5F) | 2 | U16 | 预留 (Reserve)
| 2118(0846) | 2 | U16 | 电池告警字11 BMS Alarm Word 11 | 0xFFFF | 1 | Read |  | 2778(0ADA) | 2 | U16 | 工作模式 Work Mode | 0：手动模式；1：削峰填谷模式； 2：备电模式；3、预留； 4：稳态扩容；5：瞬态扩容 | 0: Manual; 1: Peak Valley; 2: Backup Battery; 3: Reserve; 4: Steady-State Expansion; 5: Transient Expansion | 1 | Read/Write |  |  | 3424 (0D60) | 2 | U16 | 预留 (Reserve)
| 2119(0847) | 2 | U16 | 告警字5 Alarm Word 5 | 0xFFFF | 1 | Read |  | 2779(0ADB) | 2 | U16 | 电网容量 Grid capacity | [0,750] | [0,750] | 1kW | Read/Write | 仅稳态扩容模式 steady-state expansion mode only
[9 empty] | 2780(0ADC) | 2 | U16 | 电网充电SOC Grid charge SOC | [0,100] | [0,100] | 1% | Read/Write | 仅稳态扩容模式 steady-state expansion mode only
0x04 | PCS 逆变信息 PCS inverter information | [7 empty] | 2781(0ADD) | 2 | U16 | 柴发充电SOC Generator charge SOC | [0,100] | [0,100] | 1% | Read/Write | 仅稳态扩容模式 steady-state expansion mode only
| 2207(089F) | 2 | U16 | 逆变电压AB Inverter voltage AB |  | 0.1V | Read |  | 2782(0ADE) | 2 | U16 | 瞬态扩容使能位 Transient Expansion Enable Bit | 0：禁止 1：使能 | 0：Disable 1：Enable | 1 | Read/Write | 使用瞬态扩容模式必须使能该标志位 The use of transient expansion mode must enable this flag bit
| 2208(08A0) | 2 | U16 | 逆变电压BC Inverter voltage BC |  | 0.1V | Read |  | 2783(0ADF) | 2 | U16 | 充电停止SOC Charge stop SOC | [0,100] | [0,100] | 1% | Read/Write | 仅稳态扩容模式 steady-state expansion mode only
| 2209(08A1) | 2 | U16 | 逆变电压CA Inverter voltage CA |  | 0.1V | Read |  | 2784(0AE0) | 2 | U16 | 放电停止SOC Discharge stop SOC | [0,100] | [0,100] | 1% | Read/Write | 仅稳态扩容模式 steady-state expansion mode only
| 2210(08A2) | 2 | S16 | 逆变电流A Inverter current A |  | 0.1A | Read |  | 2785(0AE1) | 2 | U16 | 柴发容量 Generator Capacity | [0,750] | [0,750] | 1kW | Read/Write | 仅TS机型可用 Available for "TS" models only.
| 2211(08A3) | 2 | S16 | 逆变电流B Inverter current B |  | 0.1A | Read |  | 2786(0AE2) | 2 | U16 | 备电启动SOC Backup Battery Start Charge SOC | [0,100] | [0,100] | 1% | Read/Write | 仅备电模式 Backup Battery mode only
| 2212(08A4) | 2 | S16 | 逆变电流C Inverter current C |  | 0.1A | Read |  | 2787(0AE3) | 2 | U16 | 备电停止SOC Backup Battery Stop Charge SOC | [0,100] | [0,100] | 1% | Read/Write
| 2213(08A5) | 2 | U16 | 逆变频率（三相一致）(预留) Inverter frequency (three-phase consistent) (Reserved) |  | 0.01Hz | Read |  | 2788(0AE4) | 2 | U16 | 备电启动单体电压 Backup Battery Start Charge Cell Voltage | [2800,3600] | [2800,3600] | 1mV | Read/Write
| 2214(08A6) | 2 | S16 | PCS功率因素 PCS power factor |  | 1 | Read |  | 2789(0AE5) | 2 | U16 | 备电停止单体电压 Backup Battery Stop Charge Cell Voltage | [2800,3600] | [2800,3600] | 1mV | Read/Write
| 2215(08A7) | 2 | S16 | 逆变有功功率 Inverter active power |  | 1 | Read |  | 2790(0AE6) | 2 | U16 | 备电启动总压 Backup Battery Start Charge Total Voltage | [250,900] | [250,900] | 1V | Read/Write
| 2216(08A8) | 2 | S16 | 逆变无功功率 Inverter reactive power |  | 1 | Read |  | 2791(0AE7) | 2 | U16 | 备电停止总压 Backup Battery Stop Charge Total Voltage | [250,900] | [250,900] | 1V | Read/Write
| 2217(08A9) | 2 | S16 | 逆变视在功率 Inverted apparent power |  | 1 | Read |  | 2792(0AE8) | 2 | S16 | 备电充电功率(电网) Backup Battery Charging Power (Grid) | [-5000,-1] | [-5000,-1] | 0.1kW | Read/Write
| 2218(08AA) | 2 | S16 | 电能表总功率 Total power of energy meter |  | 0.1kW | Read |  | 2793(0AE9) | 2 | S16 | 月循环日期 Monthly cycle date | 0: 不做循环； 1~31: 每月的当日进行一次深度充放电循环 | 0: No cycle is done; 1~31: one deep charge/discharge cycle on the same day of each month | 1 | Read/Write
| 2219(08AB) | 2 | U16 | 心跳 Heartbeat |  | 1 | Read |  | 2794(0AEA) | 2 | S16 | 备电充电功率(发电机) Backup Battery Charging Power (Generator) | [-5000,-1] | [-5000,-1] | 0.1kW | Read/Write
| 2220(08AC) | 2 | U16 | 正绝缘阻抗 Positive Insulation Impedance |  | 1kΩ | Read |  | 2795(0AEB) | 2 | U16 | DC接触器辅助触点屏蔽使能 DC contactor shielding enable | 0：禁止 1：使能 | 0：Disable 1：Enable | 1 | Read/Write
| 2221(08AD) | 2 | U16 | 负绝缘阻抗 Negative Insulation Impedance |  | 1kΩ | Read |  | 2796(0AEC) | 2 | U16 | 故障恢复延时使能 Fault Recovery Delay Enable | 0：禁止 1：使能 | 0：Disable 1：Enable | 1 | Read/Write
[9 empty] | 2797(0AED) | 2 | U16 | 频繁故障拓机使能 Frequent Fault Mapping Enable | 0：禁止 1：使能 | 0：Disable 1：Enable | 1 | Read/Write
0x04 | PCS 负载侧模拟量 PCS load-side analog | [7 empty] | 2798(0AEE) | 2 | U16 | 故障重启次数设置 Fault restart frequency | [0,32767] | [0,32767] | 1 | Read/Write
| 2318(090E) | 2 | S16 | 负载电压AB Load voltage AB |  | 0.1V | Read |  | 2799(0AEF) | 2 | U16 | 消除故障命令 Eliminate fault command | 0x5555 | 0x5555 | 1 | Read/Write
| 2319(090F) | 2 | S16 | 负载电压BC Load voltage BC |  | 0.1V | Read |  | 2800(0AF0) | 2 | U16 | 变流器防逆流 Converter Anti-Reverser Flow | 0：禁止 1：使能 | 0：Disable 1：Enable | 1 | Read/Write
| 2320(0910) | 2 | S16 | 负载电压CA Load voltage CA |  | 0.1V | Read |  | 2801(0AF1) | 2 | U16 | 功率容差 power tolersnce | [0, 输出功率限制] | [0, Output power limit] | 1 | Read/Write
| 2321(0911) | 2 | S16 | 负载电流A Load current A |  | 0.1A | Read |  | 2802(0AF2) | 2 | U16 | 远程ATS信号 Remote ATS Signal | 0：未使能 1：使能 | 0：Disable 1：Enable | 1 | Read/Write
| 2322(0912) | 2 | S16 | 负载电流B Load current B |  | 0.1A | Read |  | 2803(0AF3) | 2 | U16 | 有功-频率下垂系数（预留） Active Power - Frequency Droop Coefficient(Reserve) | [0, 300] | [0, 300] | 1 | Read/Write
| 2323(0913) | 2 | S16 | 负载电流C Load current C |  | 0.1A | Read |  | 2804(0AF4) | 2 | U16 | 无功-电压下垂系数（预留） Reactive Power - Voltage Droop Coefficient(Reserve) | [0, 300] | [0, 300] | 1 | Read/Write
| 2324(0914) | 2 | U16 | 负载频率（三相一致） Load frequency (three-phase consistent) (Reserved) |  | 0.01Hz | Read |  | 2805(0AF5) | 2 | U16 | 功率限制关联方式 Power Limit Link Mode | 0：均关联 1：仅关联充电 2：仅关联放电 3：均不关联 | 0: All associated 1: Only associated with charging 2: Only associated with discharge 3: None of them are related | 1 | Read/Write
| 2325(0915) | 2 | S16 | 负载功率因数 Load Power Factor |  | 0.01 | Read |  | 2806(0AF6) | 2 | U16 | 柴发并入功率变化率 DG Power Ramp Rate | [1, 50] | [1, 50] | 1 | Read/Write
| 2326(0916) | 2 | S16 | 负载有功功率 Load Active Power |  | 0.1kW | Read |  | 2807(0AF7) | 2 | U16 | 并离网切换停机使能 Grid On/Off Switching Shutdown Enable | 0：禁止 1：使能 | 0：Disable 1：Enable | 1 | Read/Write
| 2327(0917) | 2 | S16 | 负载无功功率 Load Reactive Power |  | 0.1kvar | Read |  | 2808(0AF8) | 2 | U16 | 并离网切换停机延时时间 Grid On/Off Switching Shutdown Delay Time | [0, 100] | [0, 100] | 1 | Read/Write
| 2328(0918) | 2 | S16 | 负载视在功率 Load Apparent Power |  | 0.1kVA | Read | 0x03 0x06 | 锂电池设置参数 读取/下发 Lithium Battery Setting Parameters read/write
0x04 | PCS 电网侧模拟量 PCS grid-side analog | [7 empty] | 2882(0B42) | 2 | U16 | 并网DOD DOD_OnGrid | [10, 100] | [10, 100] | 1% | Read/Write
| 2428(097C) | 2 | S16 | 电网电压AB Grid Voltage AB |  | 0.1V | Read |  | 2883(0B43) | 2 | U16 | 离网DOD DOD_OffGrid | [5, 100] | [5, 100] | 1% | Read/Write
| 2429(097D) | 2 | S16 | 电网电压BC Grid Voltage BC |  | 0.1V | Read |  | 2884(0B44) | 2 | U16 | 充电电压上限 Charge Voltage upper Limit | [400, 1000] | [400, 850] | 1V | Read/Write
| 2430(097E) | 2 | S16 | 电网电压CA Grid Voltage CA |  | 0.1V | Read |  | 2885(0B45) | 2 | U16 | 放电电压下限 Discharge Voltage lower Limit | [400, 1000] | [400, 850] | 1V | Read/Write
| 2431(097F) | 2 | S16 | 电网电流A Grid Current A |  | 0.1A | Read |  | 2886(0B46) | 2 | U16 | 充电电流限制 Charge Current Limit | [0, 1200] | [0, 1200] | 1A | Read/Write
| 2432(0980) | 2 | S16 | 电网电流B Grid Current B |  | 0.1A | Read |  | 2887(0B47) | 2 | U16 | 预留 Reserved
| 2433(0981) | 2 | S16 | 电网电流C Grid Current C |  | 0.1A | Read |  | 2888(0B48) | 2 | U16 | 强充开启单体电压 Force Charge start voltage | [2800, 3600] | [2800, 3600] | 1mV | Read/Write
| 2434(0982) | 2 | U16 | 电网频率(三相一致) Grid frequency (three-phase consistent) |  | 0.01Hz | Read |  | 2889(0B49) | 2 | U16 | 强充停止单体电压 Force Charge stop voltage | [2800, 3600] | [2800, 3600] | 1mV | Read/Write
| 2435(0983) | 2 | S16 | 电网功率因数 Grid Power Factor |  | 0.01 | Read
| 2436(0984) | 2 | S16 | 电网有功功率 Grid Active Power |  | 0.1kW | Read
| 2437(0985) | 2 | S16 | 电网无功功率 Grid Reactive Power |  | 0.1kvar | Read
| 2438(0986) | 2 | S16 | 电网视在功率 Grid Apparent Power |  | 0.1kVA | Read
| 2439(0987) | 2 | S16 | 电能表总功率 Total power of energy meter |  | 0.1kW | Read
0x04 | PCS 模拟量 PCS Analog
| 2538(09EA) | 2 | S16 | 直流侧电压 DC side voltage |  | 0.1V | Read
| 2539(09EB) | 2 | S16 | 直流侧电流 DC side current |  | 0.1A | Read
| 2540(09EC) | 2 | S16 | 直流侧功率 DC side power |  | 0.1kW | Read
| 2541(09ED) | 2 | S16 | IGBT温度 IGBT Temperature |  | 0.1℃ | Read | 0x03 0x06 0x10 | 铅酸电池设置参数(2V一节) 读取/下发 Lead-acid battery setup parameters read/write
| 2542(09EE) | 2 | S16 | 环境温度 Ambient temperature |  | 0.1℃ | Read |  | 2988(0BAC) | 2 | U16 | 电池节数(2V) Cell number(2V) | [150,400] | [150,400] | 1 | Read/Write | 仅用于2V一节的铅酸电池 For use with 2V one cell lead-acid batteries only.
| 2543(09EF) | 2 | S16 | 预留 Reserved |  |  |  |  | 2989(0BAD) | 2 | U16 | 电池容量 Capacity | [7, 7000] | [7, 7000] | 1Ah | Read/Write
| 2544(09F0) | 2 | U16 | 当日电网放电量高位 High grid discharged volume for the day |  | 0.1kWh | Read |  | 2990(0BAE) | 2 | U16 | 充电电流限制 Charge limiting value | [2, 100] | [2, 100] | 0.01C | Read/Write
| 2545(09F1) | 2 | U16 | 当日电网放电量低位 Low grid discharged volume for the day |  | 0.1kWh | Read |  | 2991(0BAF) | 2 | U16 | 电池均充电压 Battery filling voltage | [100, 245] | [100, 245] | 0.01V | Read/Write
| 2546(09F2) | 2 | U16 | 当月电网放电量高位 High grid discharge volume for the month |  | 0.1kWh | Read |  | 2992(0BB0) | 2 | U16 | 电池浮充电压 Battery float voltage | [100, 240] | [100, 240] | 0.01V | Read/Write
| 2547(09F3) | 2 | U16 | 当月电网放电量低位 Low grid discharge volume for the month |  | 0.1kWh | Read |  | 2993(0BB1) | 2 | U16 | 并网EOD Grid on EOD | [160, 200] | [160, 200] | 0.01V | Read/Write
| 2548(09F4) | 2 | U16 | 年总电网放电量高位 High grid annual total discharge |  | 0.1kWh | Read |  | 2994(0BB2) | 2 | U16 | 离网EOD Grid off EOD | [160, 191] | [160, 191] | 0.01V | Read/Write
| 2549(09F5) | 2 | U16 | 年总电网放电量低位 Low grid annual total discharge |  | 0.1kWh | Read |  | 2995(0BB3) | 2 | U16 | 均充转浮充电流 Uniform charging and flushing current | [5, 20] | [5, 20] | 0.001C | Read/Write
| 2550(09F6) | 2 | U16 | 当日电网充电量高位 High grid charge volume for the day |  | 0.1kWh | Read |  | 2996(0BB4) | 2 | U16 | 放电电流限制 Discharge limiting value | [2, 100] | [2, 100] | 0.01C | Read/Write
| 2551(09F7) | 2 | U16 | 当日电网充电量低位 Low grid charge volume for the day |  | 0.1kWh | Read
| 2552(09F8) | 2 | U16 | 当月电网充电量高位 High grid charge volume for the month |  | 0.1kWh | Read | 0x03 0x06 0x10 | 铅酸电池设置参数(12V一节) 读取/下发 Lead-acid battery setup parameters read/write
| 2553(09F9) | 2 | U16 | 当月电网充电量低位 Low grid charging volume for the month |  | 0.1kWh | Read |  | 3030(0BD6) | 2 | U16 | 电池节数(12V) Cell number(12V) | [25, 66] | [25, 66] | 1 | Read/Write | 仅用于12V一节的铅酸电池 For use with 12V one cell lead-acid batteries only.
| 2554(09FA) | 2 | U16 | 年总电网充电量高位 High grid annual total charge volume |  | 0.1kWh | Read |  | 3031(0BD7) | 2 | U16 | 电池容量 Capacity | [7, 7000] | [7, 7000] | 1Ah | Read/Write
| 2555(09FB) | 2 | U16 | 年总电网充电量低位 Low grid annual total charge volume |  | 0.1kWh | Read |  | 3032(0BD8) | 2 | U16 | 充电电流限制 Charge limiting value | [2, 100] | [2, 100] | 0.01C | Read/Write
| 2556(09FC) | 2 | U16 | 总电网充电量高位 Total grid charge volume high |  | 0.1kWh | Read |  | 3033(0BD9) | 2 | U16 | 放电电流限制 Discharge limiting value | [2, 100] | [2, 100] | 0.01C | Read/Write
| 2557(09FD) | 2 | U16 | 总电网充电量低位 Total grid charge volume low |  | 0.1kWh | Read |  | 3034(0BDA) | 2 | U16 | 电池均充电压 Battery filling voltage | [600, 1470] | [600, 1470] | 0.01V | Read/Write
| 2558(09FE) | 2 | U16 | 总电网放电量高位 Total grid discharge volume high |  | 0.1kWh | Read |  | 3035(0BDB) | 2 | U16 | 电池浮充电压 Battery float voltage | [600, 1440] | [600, 1440] | 0.01V | Read/Write
| 2559(09FF) | 2 | U16 | 总电网放电量低位 Total grid discharge volume low |  | 0.1kWh | Read |  | 3036(0BDC) | 2 | U16 | 并网EOD Grid on EOD | [960, 1200] | [960, 1200] | 0.01V | Read/Write
| 2560(0A00) | 2 | U16 | 当日负载放电量高位 High load discharge volume for the day |  | 0.1kWh | Read |  | 3037(0BDD) | 2 | U16 | 离网EOD Grid off EOD | [960, 1200] | [960, 1200] | 0.01V | Read/Write
| 2561(0A01) | 2 | U16 | 当日负载放电量低位 Low load discharge volume for the day |  | 0.1kWh | Read |  | 3038(0BDE) | 2 | U16 | 均充转浮充电流 Equalisation to Float Current | [5, 20] | [5, 20] | 0.001C | Read/Write
| 2562(0A02) | 2 | U16 | 当月负载放电量高位 High load discharge volume for the month |  | 0.1kWh | Read |  | 3039(0BDF) | 2 | U16 | 浮充转均充电流 Floating to Equalising current | [30,700] | [30,700] | 0.001C | Read/Write
| 2563(0A03) | 2 | U16 | 当月负载放电量低位 Low load discharge volume for the month |  | 0.1kWh | Read
| 2564(0A04) | 2 | U16 | 年总负载放电量高位 High annual total load discharge volume |  | 0.1kWh | Read |  | 电池信息 Battery Information
| 2565(0A05) | 2 | U16 | 年总负载放电量低位 Low annual total load discharge volume |  | 0.1kWh | Read |  | 3097(0C19) | 2 | U16 | 电池电压 Battery voltage |  |  | 0.1V | Read/Write | 仅BMS不与PCS通信时下发 Write only when the BMS is not communicating with the PCS.
| 2566(0A06) | 2 | U16 | 总负载放电量高位 Low annual total load discharge volume |  | 0.1kWh | Read |  | 3098(0C1A) | 2 | S16 | 电池电流 Battery current |  |  | 0.1A | Read/Write
| 2567(0A07) | 2 | U16 | 总负载放电量低位 Total load discharge volume low |  | 0.1kWh | Read |  | 3099(0C1B) | 2 | U16 | SOC | [0, 100] | [0, 100] | 1% | Read/Write
| 2568(0A08) | 2 | U16 | 当日负载充电量高位 High load charge volume for the day |  | 0.1kWh | Read |  | 3100(0C1C) | 2 | U16 | SOH | [0, 100] | [0, 100] | 1% | Read/Write
| 2569(0A09) | 2 | U16 | 当日负载充电量低位 Low load charge volume for the day |  | 0.1kWh | Read |  | 3101(0C1D) | 2 | U16 | 最高单体电压 Maximum cell voltage |  |  | 1mV | Read/Write
| 2570(0A0A) | 2 | U16 | 当月负载充电量高位 High load charge volume for the month |  | 0.1kWh | Read |  | 3102(0C1E) | 2 | U16 | 最低单体电压 Minimum Cell Voltage |  |  | 1mV | Read/Write
| 2571(0A0B) | 2 | U16 | 当月负载充电量低位 Low load charge volume for the month |  | 0.1kWh | Read |  | 3103(0C1F) | 2 | U16 | 最高单体温度 Maximum cell temperature |  |  | 0.1℃ | Read/Write
| 2572(0A0C) | 2 | U16 | 年总负载充电量高位 High annual total load charge volume |  | 0.1kWh | Read |  | 3104(0C20) | 2 | U16 | 最低单体温度 Minimum cell temperature |  |  | 0.1℃ | Read/Write
| 2573(0A0D) | 2 | U16 | 年总负载充电量低位 Low annual total load charge volume |  | 0.1kWh | Read |  | 3105(0C21) | 2 | U16 | 充电电流限制 Charge current limit |  |  | 0.1A | Read/Write
| 2574(0A0E ) | 2 | U16 | 总负载充电量高位 Total load charge volume high |  | 0.1kWh | Read |  | 3106(0C22) | 2 | U16 | 放电电流限制 Discharge current limit |  |  | 0.1A | Read/Write
| 2575(0A0F) | 2 | U16 | 总负载充电量低位 Total load charge volume low |  | 0.1kWh | Read |  | 3107(0C23) | 2 | U16 | 可充电功率 Allow charge power |  |  | 1kW | Read/Write
[9 empty] | 3108(0C24) | 2 | U16 | 可放电功率 Allow discharge power |  |  | 1kW | Read/Write
[9 empty] | 3109(0C25) | 2 | U16 | 电池状态 Battery Status | 0：正常；1：禁充；2：禁放；3：告警；4：故障 | 0: Normal; 1: Charge disable; 2: Discharge disable; 3: Alarm; 4: Failure | 1 | Read/Write
[8 empty] | 0x03 0x06 0x10 | 时间设置 Time setting
[9 empty] | 3209(0C89) | 2 | U16 | 小时 Hour | [0~23] | [0~23] |  | Read/Write
[9 empty] | 3210(0C8A) | 2 | U16 | 分钟 Minute | [0~59] | [0~59] |  | Read/Write
[9 empty] | 3211(0C8B) | 2 | U16 | 秒 Seconds | [0~59] | [0~59] |  | Read/Write
[9 empty] | 3212(0C8C) | 2 | U16 | 年 Year |  |  |  | Read/Write
[9 empty] | 3213(0C8D) | 2 | U16 | 月 Month | [1~12] | [1~12] |  | Read/Write
[9 empty] | 3214(0C8E) | 2 | U16 | 日 Day | [1~31] | [1~31] |  | Read/Write
[9 empty] | 3215(0C8F) | 2 | U16 | Unix纪元秒数高16位 Unix Epoch Seconds 16 Bits Higher |  |  |  | Read/Write
[9 empty] | 3216(0C90) | 2 | U16 | Unix纪元秒数低16位 Unix Epoch Seconds 16 Bits Lower |  |  |  | Read/Write
[8 empty] | 0x03 0x06 0x10 | SN码设置(预留) SN code setting (Reserved)
[9 empty] | 3314(0CF2) | 2 | 非标F 标准 I | F1 |  |  |  | Read/Write
[9 empty] | 3315(0CF3) | 2 |  | 22 |  |  |  | Read/Write
[9 empty] | 3316(0CF4) | 2 |  | 00 |  |  |  | Read/Write
[9 empty] | 3317(0CF5) | 2 |  | 00 |  |  |  | Read/Write
[9 empty] | 3318(0CF6) | 2 |  | 00 |  |  |  | Read/Write
[9 empty] | 3319(0CF7) | 2 |  | 01 |  |  |  | Read/Write
[9 empty] | 3320(0CF8) | 2 |  | 预留 | Reserve |  |  | Read/Write
[9 empty] | 3321(0CF9) | 2 |  | 预留 | Reserve |  |  | Read/Write
[9 empty] | 3322(0CFA) | 2 |  | 预留 | Reserve |  |  | Read/Write
[9 empty] | 3323(0CFB) | 2 |  | 预留 | Reserve |  |  | Read/Write

## 状态告警字解析(Status Alarm Word Anal)
MEGA
Register (DEC/HEX) | Bit | Item | Item | Value | 备注 | Register (DEC/HEX) | Bit | Item | Item | Value | 备注 | Register (DEC/HEX) | Bit | Item | Item | Value | 备注
| 位 | 项目 | 项目 | 值 |  |  | 位 | 项目 | 项目 | 值 |  |  | 位 | 项目 | 项目 | 值
2100 (0834) 告警字1 Alarm Word 1 | Bit 0 | 变流器过流 | Converter over current | 0：正常；1：过流 0: Normal; 1: Overcurrent | PCS停机 PCS shutdown | 2101 (0835) 告警字2 Alarm Word 2 | Bit 0 | 电网过压 | Grid over voltage | 0：正常；1：过压 0: Normal; 1: Overvoltage | PCS停机 PCS shutdown | 2102 (0836) 告警字3 Alarm Word 3 | Bit 0 | 变流器故障总 | Inverter Fault Total | 0：正常；1：故障 0: Normal; 1: Fault
| Bit 1 | 变流器逐波限流 | Converter by wave current limiting | 0：正常；1：故障 0: Normal; 1: Fault | PCS停机 PCS shutdown |  | Bit 1 | 电网欠电压 | Undervoltage of Grid | 0：正常；1：欠压 0: Normal; 1: Undervoltage | PCS停机 PCS shutdown |  | Bit 1 | 变流器告警总 | Inverter Alarm Total | 0：正常；1：告警 0: Normal; 1: Alarm
| Bit 2 | 变流器故障 | Converter fault | 0：正常；1：故障 0: Normal; 1: Fault | PCS停机 PCS shutdown |  | Bit 2 | 电网电压反序 | Power grid voltage reversal | 0：正常；1：反序 0: Normal; 1: Antitone | PCS停机 PCS shutdown |  | Bit 2 - Bit 3 | 变流器开机状态总 | Inverter Startup Status Total | 0：关机；1：开机；2：待机 0: Shutdown；1: turn on；2: Standby
| Bit 3 | 电池电压低 | Low battery voltage | 0：正常；1：电压低 0: Normal; 1: Low voltage | PCS停机 PCS shutdown |  | Bit 3 | 电网频率异常 | Frequency anomaly of power grid | 0：正常；1：异常 0: Normal; 1: Abnormal | PCS停机 PCS shutdown
| Bit 4 | 电池充电不允许 | Battery charging prohibited | 0：正常；1：异常 0: Normal; 1: Abnormal | PCS停机 PCS shutdown |  | Bit 4 | 孤岛保护 | Island protection | 0：正常；1：保护 0: Normal; 1: Protection | PCS停机 PCS shutdown |  | Bit 4 | 预留 | Reserve
| Bit 5 | 并机通信故障 | Parallel communication failure | 0：正常；1：异常 0: Normal; 1: Abnormal | PCS停机 PCS shutdown |  | Bit 5 | 驱动线故障 | Drive cables fault | 0：正常；1：故障 0: Normal; 1: Fault | PCS停机 PCS shutdown |  | Bit 5 | 预留 | Reserve
| Bit 6 | 母线过压故障 | Bus over voltage fault | 0：正常；1：过压 0: Normal; 1: Overvoltage | PCS停机 PCS shutdown |  | Bit 6 | 防雷器故障 | Lightning protection fault | 0：正常；1：故障 0: Normal; 1: Fault | PCS停机 PCS shutdown |  | Bit 6 | 预留 | Reserve
| Bit 7 | 直流母线短路故障 | Bus short circuit fault | 0：正常；1：短路 0: Normal; 1: Short circuit | PCS停机 PCS shutdown |  | Bit 7 | 绝缘阻抗异常 | Abnormal insulation impedance | 0：正常；1：异常 0: Normal; 1: Abnormal | PCS停机 PCS shutdown |  | Bit 7 | 预留 | Reserve
| Bits 8 | 输出接触器开路 | Grid connected contactor open circuit | 0：正常；1：开路 0: Normal; 1: Open circuit | PCS停机 PCS shutdown |  | Bit 8 | 电池放电不允许 | Battery discharge is not allowed | 0：正常；1：故障 0: Normal; 1: Fault | 放电工况停机，电池电压放电放到放电电压下限时，PCS降功率放电 Discharge condition shutdown, battery voltage discharge to the lower limit of the discharge voltage, PCS power reduction discharge |  | Bit 8 | 预留 | Reserve
| Bit 9 | 输出接触器短路 | Grid contactor short circuit | 0：正常；1：短路 0: Normal; 1: Short circuit | PCS停机 PCS shutdown |  | Bit 9 | 逆变过压故障 | Inverter over voltage fault | 0：正常；1：故障 0: Normal; 1: Fault | PCS停机 PCS shutdown |  | Bit 9 | 预留 | Reserve
| Bit 10 | 变流器过温 | Converter over temperature | 0：正常；1：过温 0: Normal; 1: Overtemperature | PCS停机 PCS shutdown |  | Bit 10 | 15V电源故障 | 15V power failure | 0：正常；1：故障 0: Normal; 1: Fault | PCS停机 PCS shutdown |  | Bit 10 | 预留 | Reserve
| Bit 11 | 输出过载 | Over load | 0：正常；1：过载 0: Normal; 1: Overload | PCS停机 PCS shutdown |  | Bit 11 | 交流风扇故障 | AC fan failure | 0：正常；1：故障 0: Normal; 1: Fault | PCS 降额运行 PCS Derating operation |  | Bit 11 | 预留 | Reserve
| Bit 12 | 电池接反故障 | Battery reverse fault | 0：正常；1：接反 0: Normal; 1: Reverse connection | PCS停机 PCS shutdown |  | Bit 12 | 电池故障 | Battery failure | 0：正常；1：故障 0: Normal; 1: Fault | PCS停机 PCS shutdown |  | Bit 12 | 预留 | Reserve
| Bit 13 | 直流接触器故障 | DC contactor failure | 0：正常；1：故障 0: Normal; 1: Fault | PCS停机 PCS shutdown |  | Bit 13 | 紧急关机 | EPO | 0：正常；1：紧急关机 0: Normal; 1: Emergency shutdown | PCS停机 PCS shutdown |  | Bit 13 | 预留 | Reserve
| Bit 14 | BMS异常 | BMS Abnormal | 0：正常；1：故障 0: Normal; 1: Fault | PCS停机 PCS shutdown |  | Bit 14 | 变流器不同步 | Converter non synchronization | 0：正常；1：不同步 0: Normal; 1: Non synchronization | 仅告警 Alarms only |  | Bit 14 | 预留 | Reserve
| Bit 15 | 逆变器缺相故障 | Converter phase loss | 0：正常；1：故障 0: Normal; 1: Fault | PCS停机 PCS shutdown |  | Bit 15 | CT或霍尔开路故障 | CT failure | 0：正常；1：故障 0: Normal; 1: Fault | PCS停机 PCS shutdown |  | Bit 15 | 预留 | Reserve
Register (DEC/HEX) | Bit | Item | Item | Value | 备注 | Register (DEC/HEX) | Bit | Item | Item | Value | 备注 | Register (DEC/HEX) | Bit | Item | Item | Value | 备注
| 位 | 项目 | 项目 | 值 |  |  | 位 | 项目 | 项目 | 值 |  |  | 位 | 项目 | 项目 | 值
2103 (0837) 告警字4 Alarm Word 4 | Bit 0 | 预留 | Reserve |  |  | 2104 (0838) 开关状态字 Switch Status Word | Bit 0 | 直流输入断路器状态 | DC input breaker | 0：断开；1：闭合 0: Break; 1: Close |  | 2105 (0839) PCS状态字 PCS Status Word | Bit 0 | 变流器开机容许 | Converter vailable | 0：禁止； 1：使能 0: Disable；1: Enable
| Bit 1 | 预留 | Reserve |  |  |  | Bit 1 | 直流接触器状态 | DC contactor | 0：断开；1：闭合 0: Break; 2: Close |  |  | Bit 1 - Bit 2 | 直流软启动状态 | DC Soft start status | 0：未软启 0: Not starting； 1：软启动中 1: Soft starting； 2：软启完成 2: Soft Start Completed
| Bit 2 | AC电压幅值不同步 | AC voltage amplitude out of sync | 0：正常；1：不同步 0: Normal; 1: Non synchronization | PCS停机 PCS shutdown |  | Bit 2 | 输出断路器状态 | Output breaker | 0：断开；1：闭合 0: Break; 3: Close
| Bit 3 | 电池欠压 | Battery under-voltage | 0：正常；1：欠压 0: Normal; 1: Under-voltage | PCS停机 PCS shutdown |  | Bit 3 | 输出接触器状态 | Output contactor | 0：断开；1：闭合 0: Break; 4: Close |  |  | Bit 3 - Bit 5 | 变流器状态1 | Converter status | 0：关闭 0: OFF 1：软启动中 1: Soft start 2：并网充电 2: Grid-ON Charge 3：并网放电 3: Grid-ON Discharge 4：离网放电 4: Grid-OFF Discharge 5：降额并网 5: Drop and Connected 6：待机 6: Standby 7：离网充电 7: Grid-OFF Charge | 与Bit14-Bit15共同判断 Joint judgement with Bit14-Bit15
| Bit 4 | 电池过压 | Battery over-voltage | 0：正常；1：过压 0: Normal; 1: Over-voltage | PCS停机 PCS shutdown |  | Bit 4 | 电网断路器状态 | Grid breaker | 0：断开；1：闭合 0: Break; 5: Close
| Bit 5 | 电池功率低 | Low battery power | 0：正常；1：故障 0: Normal; 1: Fault | 处于放电状态时PCS机，交流接触器断开 PCS AC contactor disconnected when in the discharged state |  | Bit 5 | 电网接触器状态 | Grid contactor | 0：断开；1：闭合 0: Break; 6: Close
| Bit 6 | 母线软件过压 | Bus software over-voltage | 0：正常；1：过压 0: Normal; 1: Over-voltage | PCS停机 PCS shutdown |  | Bit 6 | 预留 | Reserve |  |  |  | Bit 6 - Bit 7 | 无功调节方式 | Reactive power regulation | 0：禁止无功调节 0: Disable 1：功率因数调节 1: Pf regulation 2：无功功率调节 2: Q regulation
| Bit 7 | 设备ID冲突 | Device ID conflict | 0：正常；1：冲突 0: Normal; 1: conflict | 仅告警 Alarms only |  | Bit 7 | 预留 | Reserve
| Bit 8 | 载波同步故障 | Carrier synchronization fault | 0：正常；1：故障 0: Normal; 1: Fault | 仅告警 Alarms only |  | Bit 8 | 预留 | Reserve |  |  |  | Bit 8 | 主从机状态 | Master/Slave Status | 0：主机 0:Master 1：从机 1:Slave
| Bit 9 | 母线硬件过压 | Bus hardware over-voltage | 0：正常；1：过压 0: Normal; 1: Over-voltage | PCS停机 PCS shutdown |  | Bit 9 | 预留 | Reserve |  |  |  | Bit 9 | 预留 | Reserve
| Bit 10 | 输出短路 | Output short circuit | 0：正常；1：短路 0: Normal; 1: Short circuit | PCS停机 PCS shutdown |  | Bit 10 | 预留 | Reserve |  |  |  | Bit 10 - Bit 12 | 逆变器控制方式 | Converter control mode | 0：预留 0：Reserve 1：预留 1：Reserve 2：恒功率 2：Constant Power 3：恒流 3：Constant Current 4：恒压 4：Constant Voltage 5：离网 5：Off grid
| Bit 11 | 并机通信故障 | Parallel communication failure | 0：正常；1：故障 0: Normal; 1: Fault | 仅告警 Alarms only |  | Bit 11 | 预留 | Reserve
| Bit 12 | 硬件过温故障 | Hardware over temperature fault | 0：正常；1：故障 0: Normal; 1: Fault | PCS停机 PCS shutdown |  | Bit 12 | 预留 | Reserve
| Bit 13 | 硬件过流 | Hardware overcurrent | 0：正常；1：故障 0: Normal; 1: Fault | PCS停机 PCS shutdown |  | Bit 13 | 预留 | Reserve |  |  |  | Bit 13 | 预留 | Reserve
| Bit 14 | 逆变过载 | Inverter overload | 0：正常；1：故障 0: Normal; 1: Fault | PCS停机 PCS shutdown |  | Bit 14 | 预留 | Reserve |  |  |  | Bit 14 - Bit 15 | 变流器状态2 | Converter status 2 | 0：变流器状态1； 0：Converter status 1 1：恒压放电； 1：Constant Voltage Discharging 2：恒压充电 2：Constant Voltage Charging | 与Bit3-Bit5共同判断 Joint judgement with Bit3-Bit5
| Bit 15 | 电池过流 | Battery overcurrent | 0：正常；1：故障 0: Normal; 1: Fault | PCS停机 PCS shutdown |  | Bit 15 | 预留 | Reserve
Register (DEC/HEX) | Bit | Item | Item | Value | 备注 | Register (DEC/HEX) | Bit | Item | Item | Value | 备注 | Register (DEC/HEX) | Bit | Item | Item | Value | 备注
| 位 | 项目 | 项目 | 值 |  |  | 位 | 项目 | 项目 | 值 |  |  | 位 | 项目 | 项目 | 值
2106 (083A) 外设状态 Peripheral Status | Bit 0 | 柴发干接点 | Diesel Generator Dry Contact | 0：关闭，1：启动 0：Break，1：Open | 输出干接点，用于启停柴发 | 2107 (083B) 监控告警字 Monitor Alarm Word | Bit 0 | 内部通信故障 | Internal communication failure | 0：正常；1：故障 0: Normal; 1: Fault | PCS停机 PCS shutdown | 2119 (0847) 告警字4 Alarm Word 4 | Bit 0 | 频繁故障拓机 | Frequent Fault Shutdown | 0：正常；1：故障 0: Normal; 1: Fault | PCS停机 PCS shutdown
| Bit 1 | 预留 | Reserve |  |  |  | Bit 1 | BMS通信故障 | BMS communication failure | 0：正常；1：故障 0: Normal; 1: Fault | PCS停机 PCS shutdown |  | Bit 1 | 预留 | Reserve
| Bit 2 | 预留 | Reserve |  |  |  | Bit2 | EMS通信故障 | EMS communication failure | 0：正常；1：故障 0: Normal; 1: Fault | PCS停机 PCS shutdown |  | Bit 2 | 预留 | Reserve
| Bit 3 | EPO关机 | EPO Shutdown | 0：禁止， 1：使能 0: Disable; 1: Enable | PCS停机 PCS shutdown |  | Bit 3 | 电能表通信故障 | Power meter communication failure | 0：正常；1：故障 0: Normal; 1: Fault | 仅提示；使用系统防逆流模式时需注意电表通信 Note only; be aware of meter communications when using the system's anti-backflow mode |  | Bit 3 | 预留 | Reserve
| Bit 4 | NC关机 | NC shutdown | 0：禁止， 1：使能 0: Disable; 1: Enable | PCS停机 PCS shutdown |  | Bit 4 | 满功率信号 | Full power signal | 0：无效， 1：有效 0: Invalid; 1: Valid | 根据PCS选择的动作响应 Response according to the action selected by PCS |  | Bit 4 | 预留 | Reserve
| Bit 5 | 门禁开启 | Access Control | 0：禁止， 1：使能 0: Disable; 1: Enable | 根据PCS选择的动作响应 Response according to the action selected by PCS |  | Bit 5 | 门禁开启 | The door open | 0：正常；1：告警 0: Normal; 1: Alarm | 根据PCS选择的动作响应 Response according to the action selected by PCS |  | Bit 5 | 预留 | Reserve
| Bit 6 | 满功率信号 | Full Power Signal | 0：禁止， 1：使能 0: Disable; 2: Enable | 根据PCS选择的动作响应 Response according to the action selected by PCS |  | Bit 6 | 烟雾告警 | Smoke Alarm | 0：正常；1：告警 0: Normal; 2: Alarm | 根据PCS选择的动作响应 Response according to the action selected by PCS |  | Bit 6 | 预留 | Reserve
| Bit 7 | 烟雾告警 | Smoke alarm | 0：禁止， 1：使能 0: Disable; 3: Enable | 根据PCS选择的动作响应 Response according to the action selected by PCS |  | Bit 7 | EPO关机 | EPO Shutdown | 0：正常；1：告警 0: Normal; 3: Alarm | 根据PCS选择的动作响应 Response according to the action selected by PCS |  | Bit 7 | 预留 | Reserve
| Bit 8 | 消防告警 (高温告警) | Temperature alarm (fire alarm) | 0：禁止， 1：使能 0: Disable; 4: Enable | 根据PCS选择的动作响应 Response according to the action selected by PCS |  | Bit8 | 干接点关机 | Dry contact shutdown | 0：无效， 1：有效 0: Invalid; 1: Valid | 根据PCS选择的动作响应 Response according to the action selected by PCS |  | Bit 8 | 预留 | Reserve
| Bit 9 | 水浸告警 | Flooding | 0：禁止， 1：使能 0: Disable; 5: Enable | 根据PCS选择的动作响应 Response according to the action selected by PCS |  | Bit 9 | 预留 | Reserve |  |  |  | Bit 9 | 预留 | Reserve
| Bit 10 | BMS告警 | BMS alarm | 0：禁止， 1：使能 0: Disable; 6: Enable | 根据PCS选择的动作响应 Response according to the action selected by PCS |  | Bit 10 | 消防告警(高温告警) | Temperature alarm (fire alarm) | 0：正常；1：告警 0: Normal; 1: Alarm | 根据PCS选择的动作响应 Response according to the action selected by PCS |  | Bit 10 | 预留 | Reserve
| Bit 11 | ATS信号 | ATS signal | 0：禁止， 1：使能 0: Disable; 7: Enable | 根据PCS选择的动作响应 Response according to the action selected by PCS |  | Bit 11 | 预留 | Reserve |  |  |  | Bit 11 | 预留 | Reserve
| Bit 12 | 预留 | Reserve |  |  |  | Bit 12 | 预留 | Reserve |  |  |  | Bit 12 | 预留 | Reserve
| Bit 13 | 预留 | Reserve |  |  |  | Bit 13 | 预留 | Reserve |  |  |  | Bit 13 | 预留 | Reserve
| Bit 14 | 预留 | Reserve |  |  |  | Bit 14 | 预留 | Reserve |  |  |  | Bit 14 | 预留 | Reserve
| Bit 15 | 预留 | Reserve |  |  |  | Bit 15 | 预留 | Reserve |  |  |  | Bit 15 | 预留 | Reserve

## BMS告警字解析(BMS Alarm Word Analys)
BMS告警字 BMS Alarm Word
Register (DEC/HEX) | Bit | Item | Item | Value | Register (DEC/HEX) | Bit | Item | Item | Value | Register (DEC/HEX) | Bit | Item | Item | Value
2108 (083C) 电池告警字1 Battery alarm word 1 | Bit 0 - Bit 1 | 单体电压过高 | Cell over voltage | 0：正常； 1：一级预警； 2：二级保护； 3：三级故障 0: normal; 1: first level of warning; 2: second level of protection; 3: third level of failure | 2109 (083D) 电池告警字2 Battery alarm word 2 | Bit 0 - Bit 1 | 单体压差过大 | Single cell voltage differential pressure large | 0：正常； 1：一级预警； 2：二级保护； 3：三级故障 0: normal; 1: first level of warning; 2: second level of protection; 3: third level of failure | 2110 (083E) 电池告警字3 Battery alarm word 3 | Bit 0 - Bit 1 | 电压传感器故障 | Voltage Sensor Error | 0：正常； 1：一级预警； 2：二级保护； 3：三级故障 0: normal; 1: first level of warning; 2: second level of protection; 3: third level of failure
| Bit 2 - Bit 3 | 单体电压过低 | Cell under voltage |  |  | Bit 2 - Bit 3 | 单体温差过大 | Battery high temperature difference |  |  | Bit 2 - Bit 3 | 温度传感器故障 | Temperature Sensor Error
| Bit 4 - Bit 5 | 单体温度过高 | Battery over temperature |  |  | Bit 4 - Bit 5 | 单体SOC过高 | Cell SOC Too High |  |  | Bit 4 - Bit 5 | 输入过压故障 | Input Over Voltage Error
| Bit 6 - Bit 7 | 单体温度过低 | Battery under temperature |  |  | Bit 6 - Bit 7 | 单体SOC过低 | Cell SOC Too Low |  |  | Bit 6 - Bit 7 | 输入反接故障 | Input Transposition Error
| Bit 8 - Bit 9 | 总电压过高 | Total voltage overvoltage |  |  | Bit 8 - Bit 9 | 绝缘故障 | Insulation Fault |  |  | Bit 8 - Bit 9 | 继电器检测故障 | Relay Check Error
| Bit 10 - Bit 11 | 总电压过低 | Total voltage undervoltage |  |  | Bit 10 - Bit 11 | BMS内部通信故障 | BMS internal communication failure |  |  | Bit 10 - Bit 11 | 电池损坏故障 | Battery cell Error
| Bit 12 - Bit 13 | 充电过流 | Charge overcurrent |  |  | Bit 12 - Bit 13 | BMS接触器异常 | BMS contactor abnormality |  |  | Bit 12 - Bit 13 | 关机电路异常 | Shutdown Circuit Error
| Bit 14 - Bit 15 | 放电过流 | Discharge overcurrent |  |  | Bit 14 - Bit 15 | BMS内部异常 | BMS internal abnormality |  |  | Bit 14 - Bit 15 | BMIC 异常 | BMIC Error
Register (DEC/HEX) | Bit | Item | Item | Value | Register (DEC/HEX) | Bit | Item | Item | Value | Register (DEC/HEX) | Bit | Item | Item | Value
2111 (083F) 电池告警字4 Battery alarm word 4 | Bit 0 - Bit 1 | 二级主控内部总线异常 | Internal bus Error | 0：正常； 1：一级预警； 2：二级保护； 3：三级故障 0: normal; 1: first level of warning; 2: second level of protection; 3: third level of failure | 2112 (0840) 电池告警字5 Battery alarm word 5 | Bit 0 - Bit 1 | 漏电流异常 | Current Leakage Error | 0：正常； 1：一级预警； 2：二级保护； 3：三级故障 0: normal; 1: first level of warning; 2: second level of protection; 3: third level of failure | 2113 (0841) 电池告警字6 Battery alarm word 6 | Bit 0 - Bit 1 | AFE芯片读取故障 | AFE Chip Reading Fault | 0：正常； 1：一级预警； 2：二级保护； 3：三级故障 0: normal; 1: first level of warning; 2: second level of protection; 3: third level of failure
| Bit 2 - Bit 3 | 开机自检电压异常 | Self-inspection Volt Error |  |  | Bit 2 - Bit 3 | 检流芯片故障 | Current IC Error |  |  | Bit 2 - Bit 3 | AFE芯片过温 | AFE Chip Overheating
| Bit 4 - Bit 5 | 安全功能异常 | Chip Error |  |  | Bit 4 - Bit 5 | 端子温度高 | Terminal High Temperature Alarm |  |  | Bit 4 - Bit 5 | AFE参考电压偏差大 | Large AFE Reference Voltage Deviation
| Bit 6 - Bit 7 | 紧急停机故障 | Emergency Stop |  |  | Bit 6 - Bit 7 | 风扇异常 | Fan Alarm |  |  | Bit 6 - Bit 7 | PACK总压压差大 | Large Total Voltage Difference Within PACK
| Bit 8 - Bit 9 | 开机自检模块串数错误 | Self-inspection Module Serial Amount Error |  |  | Bit 8 - Bit 9 | 电芯电压一致性差 | Cell Voltage Imbalance Alarm |  |  | Bit 8 - Bit 9 | PACK内电芯内阻率偏差大 | Large Internal Resistance Deviation Within PACK
| Bit 10 - Bit 11 | 开机自检模块容量错误 | Self-inspection Module Capacity Error |  |  | Bit 10 - Bit 11 | 电芯温度一致性差 | Cell Temperature Imbalance Alarm |  |  | Bit 10 - Bit 11 | PACK内电芯温升偏差大 | Large Temperature Rise Deviation Within PACK
| Bit 12 - Bit 13 | 开机自检模块初始化异常 | Self-inspection Initialize Error |  |  | Bit 12 - Bit 13 | 二级主控脱柜 | String BMS Self-disconnect Alarm |  |  | Bit 12 - Bit 13 | 簇内电芯内阻率偏差大 | Large Internal Resistance Deviation Within Cluster
| Bit 14 - Bit 15 | 模块内部总线异常 | Module internal I2C Error |  |  | Bit 14 - Bit 15 | 24V电压偏差大 | Large 24V Voltage Deviation |  |  | Bit 14 - Bit 15 | 簇内电芯温升大 | Large Temperature Rise Within Cluster
Register (DEC/HEX) | Bit | Item | Item | Value | Register (DEC/HEX) | Bit | Item | Item | Value | Register (DEC/HEX) | Bit | Item | Item | Value
2114 (0842) 电池告警字7 Battery alarm word 7 | Bit 0 - Bit 1 | 其他簇级故障 | Other Cluster Level Faults | 0：正常； 1：一级预警； 2：二级保护； 3：三级故障 0: normal; 1: first level of warning; 2: second level of protection; 3: third level of failure | 2115 (0843) 电池告警字8 Battery alarm word 8 | Bit 0 - Bit 1 | 供电过高 | High Supply Voltage | 0：正常； 1：一级预警； 2：二级保护； 3：三级故障 0: normal; 1: first level of warning; 2: second level of protection; 3: third level of failure | 2116 (0844) 电池告警字9 Battery alarm word 9 | Bit 0 - Bit 1 | 电流异常 | Abnormal Current | 0：正常； 1：一级预警； 2：二级保护； 3：三级故障 0: normal; 1: first level of warning; 2: second level of protection; 3: third level of failure
| Bit 2 - Bit 3 | BMU过温 | BMU Overheating |  |  | Bit 2 - Bit 3 | 供电过低 | Low Supply Voltage |  |  | Bit 2 - Bit 3 | 从机状态异常 | Abnormal Slave State
| Bit 4 - Bit 5 | 电流过大 | Excessive Current |  |  | Bit 4 - Bit 5 | T1高温 | High Temperature in T1 |  |  | Bit 4 - Bit 5 | 均衡温感状态异常 | Abnormal Balancing Temperature Sensing State
| Bit 6 - Bit 7 | 高压异常 | High Voltage Abnormality |  |  | Bit 6 - Bit 7 | T1低温 | Low Temperature in T1 |  |  | Bit 6 - Bit 7 | 环境温感状态异常 | Abnormal Environmental Temperature Sensing State
| Bit 8 - Bit 9 | 单体电压排线异常 | Individual Cell Voltage Line Abnormal |  |  | Bit 8 - Bit 9 | T2高温 | High Temperature in T2 |  |  | Bit 8 - Bit 9 | PCS状态异常(BMS告警位) | Abnormal PCS State(BMS Alarm Bit)
| Bit 10 - Bit 11 | 单体温感排线异常 | Individual Cell Temperature Line Abnormal |  |  | Bit 10 - Bit 11 | T2低温 | Low Temperature in T2 |  |  | Bit 10 - Bit 11 | EMS状态异常(BMS告警位) | Abnormal EMS State(BMS Alarm Bit)
| Bit 12 - Bit 13 | 预充状态异常 | Abnormal Pre-Charge State |  |  | Bit 12 - Bit 13 | 电流不均衡 | Current Imbalance |  |  | Bit 12 - Bit 13 | 保险丝状态异常 | Abnormal Fuse State
| Bit 14 - Bit 15 | 均衡过温 | Over-Temperature in Balancing |  |  | Bit 14 - Bit 15 | 高压互锁 | High Voltage Interlock |  |  | Bit 14 - Bit 15 | 模拟前端状态异常 | Abnormal Analog Front-End State
Register (DEC/HEX) | Bit | Item | Item | Value | Register (DEC/HEX) | Bit | Item | Item | Value
2117 (0845) 电池告警字10 Battery alarm word 10 | Bit 0 - Bit 1 | EEPROM状态异常 | Abnormal EEPROM State | 0：正常； 1：一级预警； 2：二级保护； 3：三级故障 0: normal; 1: first level of warning; 2: second level of protection; 3: third level of failure | 2118 (0846) 电池告警字11 Battery alarm word 11 | Bit 0 - Bit 1 | 控制指令超时 | Control Command Timeout | 0：正常； 1：一级预警； 2：二级保护； 3：三级故障 0: normal; 1: first level of warning; 2: second level of protection; 3: third level of failure
| Bit 2 - Bit 3 | RTC状态异常 | Abnormal RTC State |  |  | Bit2 - Bit3 | 预留 | Reserve
| Bit 4 - Bit 5 | ADC状态异常 | Abnormal ADC State |  |  | Bit4 - Bit5 | 预留 | Reserve
| Bit 6 - Bit 7 | SD卡状态异常 | Abnormal SD Card State |  |  | Bit6 - Bit7 | 预留 | Reserve
| Bit 8 - Bit 9 | 反馈异常 | Abnormal Feedback |  |  | Bit8 - Bit9 | 预留 | Reserve
| Bit 10 - Bit 11 | 极限故障 | Limit Fault |  |  | Bit10 - Bit11 | 预留 | Reserve
| Bit 12 - Bit 13 | 开路 | Open Circuit |  |  | Bit12 - Bit13 | 预留 | Reserve
| Bit 14 - Bit 15 | 消防异常 | Fire Protection Abnormal |  |  | Bit14 - Bit15 | 预留 | Reserve